## Slide 1: Energy Networks Association
ENA EREC G69 Issue 5 2026
Revision Summary
15th April 2026

## Slide 2: ENA EREC G69 Issue 5 2026 Revision Summary
Guidance on working with insulation and interruption gases (IIG) used in electrical power equipment
To collate key requirements, guidance and best practice for working with insulation and interruption gases (IIG) for use in electric power equipment. This includes pure IIG and IIG mixtures
  SCOPE
    Background on use of IIGs in electric power equipment.
    UK and European legislation relating to use of IIGs
    Properties of different types of IIGs covered by EREC.
    Impact of IIGs on the environment.
    Toxicology and hazards of IIGs.
    Guidance on storage, transport and handling procedures for IIGs used in electric power equipment.
  HISTORY
DOCUMENT PURPOSE
2
Issue No. | Date | Details of revision.
1st Issue | 2005 | First Issue.
Issue 2 | 2012 | Updated after publication of F-Gas Regs 2009.
Issue 3 | 2013 | Minor revision to incorporate information from EREC G72.
Issue 3 + Amdt. 1 | 2016 | Updated due to introduction of F-Gas Regs 2015 and new Ofgem reporting requirements.
Issue 4 | 2022 | Major update to include wider range of IIGs, changes to legislation, Ofgem requirements and revision BS EN IEC 62271-4.

## Slide 3
Summary of Amendments
    Title of document changed from:
      “Guidance on working with Insulation and Interruption Gas (IIG) and gas mixtures in high voltage switchgear of rated voltage up to and including 145 kV” to..
      “Guidance on working with insulation and interruption gases (IIG) used in electric power equipment”
      This reflects terminology used in BS EN IEC 62271-4
      Updated references to Standards, legislation and other manufacturer guidance documents that been issued since Issue 4:
      EU F-Gas Regulations 2024. These regulations are presently not adopted in GB but are considered as best practice by parties such as Ofgem
      Ofgem Greenhouse Gas (GHG) revised reporting requirements for ENA Member Companies under recent Price Review settlements
EU F-Gas Regs 2024 lays down dates for ban of use of F-gases in electrical power equipment depending on voltage range
These Regs not adopted by GB under F-Gas EU Exit Regulations 2021 but apply to Northern Ireland
Ofgem now require reporting on all IIGs with GWP >0
Major
Key Points
Nature of Revision
3
ENA EREC G69 Issue 5 2026 Revision Summary

## Slide 4
Summary of Amendments
    Publication of BS EN IEC 63360, which specifies the quality of alternative gases to SF6 for use in electrical power equipment, including:
      Compressed air
      Synthetic air
      Natural-origin gases
      C5-FK (C5F10O) Fluoroketone gas mixtures
      C4-FN (C4F7N) Fluoronitrile gas mixtures
    Draft BS EN IEC 63359:
      Specifies the quality of above alternative gases to SF6 for their re-use in electric power equipment after recovery
      At CDV stage at time of revision of Issue 5 of EREC G69. Expected to be issued in 2026
These Standards specify the quality of IIGs for use in electric power equipment
Concentration level
Maximum moisture content
Impurities
Requirements now incorporated into Issue 5 or EREC G69
Major
Key Points
Nature of Revision
4
ENA EREC G69 Issue 5 2026 Revision Summary

## Slide 5
Summary of Amendments
    Sections covering C4-FN mixtures have been revised to provide more information on the use and handling of C4-FN mixtures
      Protection against asphyxiation
      Precautions to prevent exposure to solid-by products in C4-FN mixtures
      Precautions to prevent exposure to C4-FN
      Precautions to prevent exposure to CO
Some specialist PPE is required when working with non-arced C4-FN mixtures
May contain Fluoro-amide crystals which are toxic when ingested but will also cause eye and skin irritation
Maximum levels for exposure to C4-FN mixtures specified
Different PPE recommended for different work activities
Major
Key Points
Nature of Revision
5
ENA EREC G69 Issue 5 2026 Revision Summary

## Slide 6
Summary of Amendments
    Guidance now provided on notices to be posted at substations containing IIGs:
For member companies who already display SF6 notices at sites:
New notices recommended
For natural-origin gases with O2 < 19.5%
Recommended notices also for sites with C4-FN or C5-FK nixtures
Major
Key Points
Nature of Revision
6
ENA EREC G69 Issue 5 2026 Revision Summary

## Slide 7
Who is affected and why?
    Primarily, staff and contractors, who are tasked with handling of IIG in electric power equipment (mainly in HV switchgear) during gas recovery, gas filling and topping up of gas -New procedures now required for C4-FN mixtures.
    Operational staff who operate switchgear (particularly precautions to be taken in event of a large loss of IIG or an internal arcing fault) – Staff need to be aware of possible hazards and procedures /PPE to be implemented. Also steps needed to avoid leakage of some IIGs to the environment.
    Staff involved in the transport of electric power equipment containing IIG- Need to be aware of maximum thresholds before special transport measures are needed.
    Staff involved in the storage of IIG in containers and cylinders- procedures for checking leakage and preventing leakages
7
ENA EREC G69 Issue 5 2026 Revision Summary

## Slide 8
 | Rating | Assessment
Safety | Major | Additional guidance on handling of gases needed.
Environment | Major | Alternative IIGs with lower GWPs compared to SF6 now covered but leakage of some IIGs (e.g. C4-FN) still need to be avoided.
Financial (costs/benefits) | Medium | Significant training costs and new IIG handling equipment may be required.
Asset Quality & Performance | Medium | Failure to comply with quality requirements of IIG may lead to reduced asset life or failure of asset in service.
Statutory/ Regulatory | Medium | Changes to statutory requirements for use of IIGs in Northern Ireland (likely to be introduced into GB in near future).
Reputation | Major | Failure to comply with the requirements specified in this EREC can lead to loss of IIG to the atmosphere with risk of significant impact on reputation.
Impact Assessment
8
ENA EREC G69 Issue 5 2026 Revision Summary

## Slide 9
Summary and Actions
    ENA EREC G69 Issue 5 2026 is a major revision of Issue 4
    ENA Member Companies may to review their relevant documentation and operating procedures for handling of IIG in electric power equipment
    The document is available from the ENA Engineering Catalogue at: www.energynetworks.org.
9
ENA EREC G69 Issue 5 2026 Revision Summary

## Slide 10
© ENA 2026
10