## Slide 1: Energy Networks Association
ENA TS 35-1 Part 2 Issue 7 2021
Revision Summary
2 December 2021

## Slide 2: ENA TS 35-1 Part 2 Issue 7 2021 Revision Summary
Distribution Transformers
Part 2 Ground mounted transformers—not close-coupled
This Specification applies to transformers in the range 50 kVA to 2 000 kVA for continuous service at 50 Hz, for highest voltage for equipment 7.2 kV, 12 kV, and 24 kV
Part 2 of the specification includes requirements for not close-coupled, ground mounted transformers
  SCOPE
  Applies to single-phase and three-phase, two-winding, liquid-immersed, naturally cooled transformers suitable in all respects for indoor or outdoor service connected by oil/air bushings, oil/oil bushings or bushings into cable boxes or separable connectors.
  Presents the requirements which must be satisfied for ground-mounted transformers that are not designed for mounting of close-coupled switchgear
  HISTORY
    1st issued: not known
    Last revision Issue 6 in 2014
DOCUMENT PURPOSE
2

## Slide 3: ENA TS 35-1 Part 2 Issue 7 2021 Revision Summary
Summary of Amendments
    Normative references and bibliography documents have been updated to reflect current issue status.
    Options for terminations on same side has been removed as this is not a standard layout for transformers without close-coupled switchgear.
    Option for cable box on cover has been added.
    Details of earthing bar in cable boxes has been added.
    Options for cable box on cover or shrouded terminations added.
    With increasing numbers of voltage-regulating distribution transformers being connected to the system, a new clause for on-load tapchanger has been added.
    New clause for control methods and interface with Network Management System added, as part of requirements for on-load tapchangers.
Normative references updated
Option for cable boxes on same side removed
Option for cable boxes on cover added
Requirements for on-load tapchangers included
Medium
Key Points
Nature of Revision
3

## Slide 4: ENA TS 35-1 Part 2 Issue 7 2021 Revision Summary
Who is affected and why?
    ENA Member Companies should review their purchase specifications for transformers in the range 16 kVA to 2 000 kVA for continuous service at 50 Hz, for highest voltage for equipment 7.2 kV, 12 kV, 24 kV and 36 kV against the revised TS 35-1 and update, as necessary
    The changes made to TS 35-1 Part 2 enhance the design requirements for distribution transformers without close-coupled switchgear
4

## Slide 5: ENA TS 35-1 Part 2 Issue 7 2021 Revision Summary
 | Rating | Assessment
Safety | Minor | Cable boxes on same side can constitute a safety risk; option has been removed except for cases where site layout does not permit other options
Environment | Nil | 
Financial (costs/benefits) | Nil | 
Asset Quality & Performance | Minor | Option for on-load tapchanger will enhance the network performance with embedded generation
Statutory/ Regulatory | Nil | Statutory requirements unchanged
Reputation | Minor | The document is outdated with respect to some standards and innovation and could damage the reputation of ENA Member companies if not updated.
Impact Assessment
5

## Slide 6: ENA TS 35-1 Part 2 Issue 7 2021 Revision Summary
Summary and Actions
    ENA TS 35-1 Part 2 Issue 7 2021is a medium revision of Issue 6
    ENA Member Companies to review their relevant documentation and operating procedures for the procurement, approval, use, storage, transport, and inspection of distribution transformers
    The document is available from the ENA Engineering Catalogue at www.energynetworks.org.
6

## Slide 7
© ENA 2020
7