## Slide 1: Energy Networks Association
ENA TS 97-1 Issue 3 2021
Revision Summary
01 December 2021

## Slide 2: ENA TS 97-1 Issue 3 2021 Revision Summary
Special backfill material for cable installations
To ensure that any backfill materials placed in a cable trench have thermal resistivities in the dried-out state that do not exceed the limiting values assigned by the Contractor or specified by the Network Owner in the design of the cable installation
  SCOPE
  To set out the general requirements for special backfill materials, both currently acceptable types of stabilised backfill materials and the option for alternative cable surround materials, which allow the designated ratings for the cable to be applied.
  The Specification applies to backfill materials that are intended for open trench applications, where the cable is either directly buried in the backfill or installed in ducts laid in the backfill, and, as such, the backfills are required to be load bearing, resist settlement, erosion, impact and frost heave.
  HISTORY
  1st issued: 1997
  2016: Major revision to reflect changes made to the standards referenced and to allow the option for novel cable backfill materials to be utilised by specifying the performance characteristics required for such backfill materials
  2021: Minor revision as detailed overleaf
PURPOSE

## Slide 3: ENA TS 12-2 Issue 3 2021 Revision Summary
Summary of Amendments
  Portland cement specification for use in Cement Bound Sand backfill amended by removing requirement to use of 32.5 N strength class
  Additional requirements for alternative backfill materials:
      Backfill materials that would impede the subsequent removal of the backfill are not acceptable, unless approved by the Engineer
      Foam concrete not to be used as a void filler or in reinstatement of a cable trench, unless approved by the Engineer
  When type testing alternative backfill material, measurement of thermal resistivity amended by removing restriction to use only BS EN ISO 8990
Amendment to specifications for:
- Cement Bound Sand backfill
- Alternative backfill materials
Minor
Key Points
Nature of Revision

## Slide 4: ENA TS 97-1 Issue 3 2021 Revision Summary
Who is affected and why?
  Staff and cable contractors, who are tasked with the procurement and/or installation of special backfill materials for cable installations
  Relevant staff should be advised of the amendments to the specifications for Cement Bound Sand and Alternative backfill materials

## Slide 5: ENA TS 97-1 Issue 3 2021 Revision Summary
 | Rating | Assessment
Safety | Nil | No impact
Environment | Nil | No impact
Financial (costs/benefits) | Nil | No changes to requirements
Asset Quality & Performance | Minor | Amendment to specification for alternative backfills avoid possible difficulties with their subsequent removal, due to use of overly strong materials and detrimental thermal performance of cable from use of foam concrete
Statutory/ Regulatory | Nil | No impact
Reputation | Nil | No impact
Impact Assessment

## Slide 6: ENA TS 97-1 Issue 3 2021 Revision Summary
Summary and Actions
  ENA TS 97-1 Issue 2021 is a minor revision of Issue 2
  Minor amendments to specification for Cement Bound sand backfills and Alternative backfill materials
  Relevant staff should be made aware of the amendments
    The document is available from the ENA Engineering Catalogue at www.energynetworks.org.

## Slide 7
© ENA 2021