## Table C.1_Single Phase
ENA TS 48-6-1, Dynamic Tests - Single Phase to Earth Faults
Test Reference | Fault Type | Phase | POW (Deg.) | Fault Location | Fault Level | Load Flow (MW) | Rf | Test Results
[7 empty] | ɸ-E | Test 1 |  | Test 2 |  | Test 3 |  | Test 4 |  | Test 5 |  | Min. Operate Time | Max. Operate Time | Ave. Operate Time
[8 empty] | Operate Time | Prot. Element | Operate Time | Prot. Element | Operate Time | Prot. Element | Operate Time | Prot. Element | Operate Time | Prot. Element
C1.A-E | ɸ-E | A-E | 0 | F1 |  |  | 0
C1.B-E | ɸ-E | B-E | 0 | F1 |  |  | 0
C1.C-E | ɸ-E | C-E | 0 | F1 |  |  | 0
C2.A-E | ɸ-E | A-E | 90 | F1 |  |  | 0
C2.B-E | ɸ-E | B-E | 90 | F1 |  |  | 0
C2.C-E | ɸ-E | C-E | 90 | F1 |  |  | 0
C3.A-E | ɸ-E | A-E | 0 | F1 |  |  | 5
C3.B-E | ɸ-E | B-E | 0 | F1 |  |  | 5
C3.C-E | ɸ-E | C-E | 0 | F1 |  |  | 5
C4.A-E | ɸ-E | A-E | 0 | F1 |  |  | 10
C4.B-E | ɸ-E | B-E | 0 | F1 |  |  | 10
C4.C-E | ɸ-E | C-E | 0 | F1 |  |  | 10
C5.A-E | ɸ-E | A-E | 0 | F2 |  |  | 0
C5.B-E | ɸ-E | B-E | 0 | F2 |  |  | 0
C5.C-E | ɸ-E | C-E | 0 | F2 |  |  | 0
C6.A-E | ɸ-E | A-E | 90 | F2 |  |  | 0
C6.B-E | ɸ-E | B-E | 90 | F2 |  |  | 0
C6.C-E | ɸ-E | C-E | 90 | F2 |  |  | 0
C7.A-E | ɸ-E | A-E | 0 | F2 |  |  | 5
C7.B-E | ɸ-E | B-E | 0 | F2 |  |  | 5
C7.C-E | ɸ-E | C-E | 0 | F2 |  |  | 5
C8.A-E | ɸ-E | A-E | 0 | F2 |  |  | 10
C8.B-E | ɸ-E | B-E | 0 | F2 |  |  | 10
C8.C-E | ɸ-E | C-E | 0 | F2 |  |  | 10
C9.A-E | ɸ-E | A-E | 0 | F2 |  |  | 100
C9.B-E | ɸ-E | B-E | 0 | F2 |  |  | 100
C9.C-E | ɸ-E | C-E | 0 | F2 |  |  | 100
C10.A-E | ɸ-E | A-E | 0 | F3 |  |  | 0
C10.B-E | ɸ-E | B-E | 0 | F3 |  |  | 0
C10.C-E | ɸ-E | C-E | 0 | F3 |  |  | 0
C11.A-E | ɸ-E | A-E | 90 | F3 |  |  | 0
C11.B-E | ɸ-E | B-E | 90 | F3 |  |  | 0
C11.C-E | ɸ-E | C-E | 90 | F3 |  |  | 0
C12.A-E | ɸ-E | A-E | 180 | F3 |  |  | 0
C12.B-E | ɸ-E | B-E | 180 | F3 |  |  | 0
C12.C-E | ɸ-E | C-E | 180 | F3 |  |  | 0
C13.A-E | ɸ-E | A-E | 0 | F3 |  |  | 2
C13.B-E | ɸ-E | B-E | 0 | F3 |  |  | 2
C13.C-E | ɸ-E | C-E | 0 | F3 |  |  | 2
C14.A-E | ɸ-E | A-E | 0 | F3 |  |  | 5
C14.B-E | ɸ-E | B-E | 0 | F3 |  |  | 5
C14.C-E | ɸ-E | C-E | 0 | F3 |  |  | 5
C15.A-E | ɸ-E | A-E | 90 | F3 |  |  | 5
C15.B-E | ɸ-E | B-E | 90 | F3 |  |  | 5
C15.C-E | ɸ-E | C-E | 90 | F3 |  |  | 5
C16.A-E | ɸ-E | A-E | 0 | F3 |  |  | 10
C16.B-E | ɸ-E | B-E | 0 | F3 |  |  | 10
C16.C-E | ɸ-E | C-E | 0 | F3 |  |  | 10
C17.A-E | ɸ-E | A-E | 0 | F3 |  |  | 50
C17.B-E | ɸ-E | B-E | 0 | F3 |  |  | 50
C17.C-E | ɸ-E | C-E | 0 | F3 |  |  | 50
C18.A-E | ɸ-E | A-E | 0 | F3 |  |  | 100
C18.B-E | ɸ-E | B-E | 0 | F3 |  |  | 100
C18.C-E | ɸ-E | C-E | 0 | F3 |  |  | 100
C19.A-E | ɸ-E | A-E | 0 | F4 |  |  | 0
C19.B-E | ɸ-E | B-E | 0 | F4 |  |  | 0
C19.C-E | ɸ-E | C-E | 0 | F4 |  |  | 0
C20.A-E | ɸ-E | A-E | 90 | F4 |  |  | 0
C20.B-E | ɸ-E | B-E | 90 | F4 |  |  | 0
C20.C-E | ɸ-E | C-E | 90 | F4 |  |  | 0
C21.A-E | ɸ-E | A-E | 180 | F4 |  |  | 0
C21.B-E | ɸ-E | B-E | 180 | F4 |  |  | 0
C21.C-E | ɸ-E | C-E | 180 | F4 |  |  | 0
C22.A-E | ɸ-E | A-E | 0 | F4 |  |  | 2
C22.B-E | ɸ-E | B-E | 0 | F4 |  |  | 2
C22.C-E | ɸ-E | C-E | 0 | F4 |  |  | 2
C23.A-E | ɸ-E | A-E | 0 | F4 |  |  | 5
C23.B-E | ɸ-E | B-E | 0 | F4 |  |  | 5
C23.C-E | ɸ-E | C-E | 0 | F4 |  |  | 5
C24.A-E | ɸ-E | A-E | 90 | F4 |  |  | 5
C24.B-E | ɸ-E | B-E | 90 | F4 |  |  | 5
C24.C-E | ɸ-E | C-E | 90 | F4 |  |  | 5
C25.A-E | ɸ-E | A-E | 0 | F4 |  |  | 10
C25.B-E | ɸ-E | B-E | 0 | F4 |  |  | 10
C25.C-E | ɸ-E | C-E | 0 | F4 |  |  | 10
C26.A-E | ɸ-E | A-E | 0 | F4 |  |  | 50
C26.B-E | ɸ-E | B-E | 0 | F4 |  |  | 50
C26.C-E | ɸ-E | C-E | 0 | F4 |  |  | 50
C27.A-E | ɸ-E | A-E | 0 | F5 |  |  | 0
C27.B-E | ɸ-E | B-E | 0 | F5 |  |  | 0
C27.C-E | ɸ-E | C-E | 0 | F5 |  |  | 0
C28.A-E | ɸ-E | A-E | 180 | F5 |  |  | 0
C28.B-E | ɸ-E | B-E | 180 | F5 |  |  | 0
C28.C-E | ɸ-E | C-E | 180 | F5 |  |  | 0
C29.A-E | ɸ-E | A-E | 0 | F5 |  |  | 10
C29.B-E | ɸ-E | B-E | 0 | F5 |  |  | 10
C29.C-E | ɸ-E | C-E | 0 | F5 |  |  | 10
C30.A-E | ɸ-E | A-E | 0 | F5 |  |  | 50
C30.B-E | ɸ-E | B-E | 0 | F5 |  |  | 50
C30.C-E | ɸ-E | C-E | 0 | F5 |  |  | 50
C31.A-E | ɸ-E | A-E | 0 | F6 |  |  | 0
C31.B-E | ɸ-E | B-E | 0 | F6 |  |  | 0
C31.C-E | ɸ-E | C-E | 0 | F6 |  |  | 0
C32.A-E | ɸ-E | A-E | 90 | F6 |  |  | 0
C32.B-E | ɸ-E | B-E | 90 | F6 |  |  | 0
C32.C-E | ɸ-E | C-E | 90 | F6 |  |  | 0
C33.A-E | ɸ-E | A-E | 0 | F6 |  |  | 10
C33.B-E | ɸ-E | B-E | 0 | F6 |  |  | 10
C33.C-E | ɸ-E | C-E | 0 | F6 |  |  | 10
C34.A-E | ɸ-E | A-E | 0 | F7 |  |  | 0
C34.B-E | ɸ-E | B-E | 0 | F7 |  |  | 0
C34.C-E | ɸ-E | C-E | 0 | F7 |  |  | 0
C35.A-E | ɸ-E | A-E | 90 | F7 |  |  | 0
C35.B-E | ɸ-E | B-E | 90 | F7 |  |  | 0
C35.C-E | ɸ-E | C-E | 90 | F7 |  |  | 0
C36.A-E | ɸ-E | A-E | 0 | F7 |  |  | 10
C36.B-E | ɸ-E | B-E | 0 | F7 |  |  | 10
C36.C-E | ɸ-E | C-E | 0 | F7 |  |  | 10
C37.A-E | ɸ-E | A-E | 0 | F8 |  |  | 0
C37.B-E | ɸ-E | B-E | 0 | F8 |  |  | 0
C37.C-E | ɸ-E | C-E | 0 | F8 |  |  | 0
C38.A-E | ɸ-E | A-E | 90 | F8 |  |  | 0
C38.B-E | ɸ-E | B-E | 90 | F8 |  |  | 0
C38.C-E | ɸ-E | C-E | 90 | F8 |  |  | 0
C39.A-E | ɸ-E | A-E | 0 | F8 |  |  | 10
C39.B-E | ɸ-E | B-E | 0 | F8 |  |  | 10
C39.C-E | ɸ-E | C-E | 0 | F8 |  |  | 10
| Tests | x5
Model A1 |  |  |  | Key:
C1 Count: | 117 | 585 |  | Rf - | Fault Resistance |  | (ohms)
C1 to C6 Count: | 362 | 1810 |  | ɸ - | Phase |  | (A, B, C) or (L1, L2, L3)
|  |  |  | E - | Earth

## Table C.2_Phase - Phase
ENA TS 48-6-1, Dynamic Tests - Phase to Phase Faults
Test Reference | Fault Type | Phases | POW (Deg.) | Fault Location | Fault Level | Load Flow (MW) | Rf | Test Results
[7 empty] | ɸ-ɸ | Test 1 |  | Test 2 |  | Test 3 |  | Test 4 |  | Test 5 |  | Min. Operate Time | Max. Operate Time | Ave. Operate Time
[8 empty] | Operate Time | Prot. Element | Operate Time | Prot. Element | Operate Time | Prot. Element | Operate Time | Prot. Element | Operate Time | Prot. Element
C40.A-B | ɸ-ɸ | A-B | 0 | F1 |  |  | 0
C40.B-C | ɸ-ɸ | B-C | 0 | F1 |  |  | 0
C40.C-A | ɸ-ɸ | C-A | 0 | F1 |  |  | 0
C41.A-B | ɸ-ɸ | A-B | 90 | F1 |  |  | 0
C41.B-C | ɸ-ɸ | B-C | 90 | F1 |  |  | 0
C41.C-A | ɸ-ɸ | C-A | 90 | F1 |  |  | 0
C42.A-B | ɸ-ɸ | A-B | 0 | F1 |  |  | 5
C42.B-C | ɸ-ɸ | B-C | 0 | F1 |  |  | 5
C42.C-A | ɸ-ɸ | C-A | 0 | F1 |  |  | 5
C43.A-B | ɸ-ɸ | A-B | 0 | F1 |  |  | 10
C43.B-C | ɸ-ɸ | B-C | 0 | F1 |  |  | 10
C43.C-A | ɸ-ɸ | C-A | 0 | F1 |  |  | 10
C44.A-B | ɸ-ɸ | A-B | 0 | F2 |  |  | 0
C44.B-C | ɸ-ɸ | B-C | 0 | F2 |  |  | 0
C44.C-A | ɸ-ɸ | C-A | 0 | F2 |  |  | 0
C45.A-B | ɸ-ɸ | A-B | 90 | F2 |  |  | 0
C45.B-C | ɸ-ɸ | B-C | 90 | F2 |  |  | 0
C45.C-A | ɸ-ɸ | C-A | 90 | F2 |  |  | 0
C46.A-B | ɸ-ɸ | A-B | 0 | F2 |  |  | 5
C46.B-C | ɸ-ɸ | B-C | 0 | F2 |  |  | 5
C46.C-A | ɸ-ɸ | C-A | 0 | F2 |  |  | 5
C47.A-B | ɸ-ɸ | A-B | 0 | F2 |  |  | 10
C47.B-C | ɸ-ɸ | B-C | 0 | F2 |  |  | 10
C47.C-A | ɸ-ɸ | C-A | 0 | F2 |  |  | 10
C48.A-B | ɸ-ɸ | A-B | 0 | F3 |  |  | 0
C48.B-C | ɸ-ɸ | B-C | 0 | F3 |  |  | 0
C48.C-A | ɸ-ɸ | C-A | 0 | F3 |  |  | 0
C49.A-B | ɸ-ɸ | A-B | 90 | F3 |  |  | 0
C49.B-C | ɸ-ɸ | B-C | 90 | F3 |  |  | 0
C49.C-A | ɸ-ɸ | C-A | 90 | F3 |  |  | 0
C50.A-B | ɸ-ɸ | A-B | 180 | F3 |  |  | 0
C50.B-C | ɸ-ɸ | B-C | 180 | F3 |  |  | 0
C50.C-A | ɸ-ɸ | C-A | 180 | F3 |  |  | 0
C51.A-B | ɸ-ɸ | A-B | 0 | F3 |  |  | 5
C51.B-C | ɸ-ɸ | B-C | 0 | F3 |  |  | 5
C51.C-A | ɸ-ɸ | C-A | 0 | F3 |  |  | 5
C52.A-B | ɸ-ɸ | A-B | 0 | F3 |  |  | 10
C52.B-C | ɸ-ɸ | B-C | 0 | F3 |  |  | 10
C52.C-A | ɸ-ɸ | C-A | 0 | F3 |  |  | 10
C53.A-B | ɸ-ɸ | A-B | 0 | F4 |  |  | 0
C53.B-C | ɸ-ɸ | B-C | 0 | F4 |  |  | 0
C53.C-A | ɸ-ɸ | C-A | 0 | F4 |  |  | 0
C54.A-B | ɸ-ɸ | A-B | 90 | F4 |  |  | 0
C54.B-C | ɸ-ɸ | B-C | 90 | F4 |  |  | 0
C54.C-A | ɸ-ɸ | C-A | 90 | F4 |  |  | 0
C55.A-B | ɸ-ɸ | A-B | 180 | F4 |  |  | 0
C55.B-C | ɸ-ɸ | B-C | 180 | F4 |  |  | 0
C55.C-A | ɸ-ɸ | C-A | 180 | F4 |  |  | 0
C56.A-B | ɸ-ɸ | A-B | 0 | F4 |  |  | 5
C56.B-C | ɸ-ɸ | B-C | 0 | F4 |  |  | 5
C56.C-A | ɸ-ɸ | C-A | 0 | F4 |  |  | 5
C57.A-B | ɸ-ɸ | A-B | 0 | F4 |  |  | 10
C57.B-C | ɸ-ɸ | B-C | 0 | F4 |  |  | 10
C57.C-A | ɸ-ɸ | C-A | 0 | F4 |  |  | 10
C58.A-B | ɸ-ɸ | A-B | 0 | F5 |  |  | 0
C58.B-C | ɸ-ɸ | B-C | 0 | F5 |  |  | 0
C58.C-A | ɸ-ɸ | C-A | 0 | F5 |  |  | 0
C59.A-B | ɸ-ɸ | A-B | 90 | F5 |  |  | 0
C59.B-C | ɸ-ɸ | B-C | 90 | F5 |  |  | 0
C59.C-A | ɸ-ɸ | C-A | 90 | F5 |  |  | 0
C60.A-B | ɸ-ɸ | A-B | 0 | F5 |  |  | 5
C60.B-C | ɸ-ɸ | B-C | 0 | F5 |  |  | 5
C60.C-A | ɸ-ɸ | C-A | 0 | F5 |  |  | 5
C61.A-B | ɸ-ɸ | A-B | 0 | F5 |  |  | 10
C61.B-C | ɸ-ɸ | B-C | 0 | F5 |  |  | 10
C61.C-A | ɸ-ɸ | C-A | 0 | F5 |  |  | 10
C62.A-B | ɸ-ɸ | A-B | 0 | F6 |  |  | 0
C62.B-C | ɸ-ɸ | B-C | 0 | F6 |  |  | 0
C62.C-A | ɸ-ɸ | C-A | 0 | F6 |  |  | 0
C63.A-B | ɸ-ɸ | A-B | 90 | F6 |  |  | 0
C63.B-C | ɸ-ɸ | B-C | 90 | F6 |  |  | 0
C63.C-A | ɸ-ɸ | C-A | 90 | F6 |  |  | 0
C64.A-B | ɸ-ɸ | A-B | 0 | F6 |  |  | 5
C64.B-C | ɸ-ɸ | B-C | 0 | F6 |  |  | 5
C64.C-A | ɸ-ɸ | C-A | 0 | F6 |  |  | 5
C65.A-B | ɸ-ɸ | A-B | 0 | F6 |  |  | 10
C65.B-C | ɸ-ɸ | B-C | 0 | F6 |  |  | 10
C65.C-A | ɸ-ɸ | C-A | 0 | F6 |  |  | 10
| Tests | x5
Model A1 |  |  |  | Key:
C2 Count: | 78 | 390 |  | Rf - | Fault Resistance |  | (ohms)
|  |  |  | ɸ - | Phase |  | (A ,B, C) or (L1, L2, L3)
|  |  |  | E - | Earth

## Table C.3_Phase-Phase-Earth
ENA TS 48-6-1, Dynamic Tests - Phase to Phase to Earth Faults
Test Reference | Fault Type | Phases | POW (Deg.) | Fault Location | Fault Level | Load Flow (MW) | Rf (W) |  | Test Results
[7 empty] | ɸ-ɸ | ɸ-E(1) | Test 1 |  | Test 2 |  | Test 3 |  | Test 4 |  | Test 5 |  | Min. Operate Time | Max. Operate Time | Ave. Operate Time
[9 empty] | Operate Time | Prot. Element | Operate Time | Prot. Element | Operate Time | Prot. Element | Operate Time | Prot. Element | Operate Time | Prot. Element
C66.A-B-E | ɸ-ɸ-E | A-B-E | 0 | F1 |  |  | 0 | 0
C66.B-C-E | ɸ-ɸ-E | B-C-E | 0 | F1 |  |  | 0 | 0
C66.C-A-E | ɸ-ɸ-E | C-A-E | 0 | F1 |  |  | 0 | 0
C67.A-B-E | ɸ-ɸ-E | A-B-E | 0 | F1 |  |  | 5 | 0
C67.B-C-E | ɸ-ɸ-E | B-C-E | 0 | F1 |  |  | 5 | 0
C67.C-A-E | ɸ-ɸ-E | C-A-E | 0 | F1 |  |  | 5 | 0
C68.A-B-E | ɸ-ɸ-E | A-B-E | 0 | F1 |  |  | 5 | 10
C68.B-C-E | ɸ-ɸ-E | B-C-E | 0 | F1 |  |  | 5 | 10
C68.C-A-E | ɸ-ɸ-E | C-A-E | 0 | F1 |  |  | 5 | 10
C69.A-B-E | ɸ-ɸ-E | A-B-E | 0 | F3 |  |  | 0 | 0
C69.B-C-E | ɸ-ɸ-E | B-C-E | 0 | F3 |  |  | 0 | 0
C69.C-A-E | ɸ-ɸ-E | C-A-E | 0 | F3 |  |  | 0 | 0
C70.A-B-E | ɸ-ɸ-E | A-B-E | 0 | F3 |  |  | 0 | 5
C70.B-C-E | ɸ-ɸ-E | B-C-E | 0 | F3 |  |  | 0 | 5
C70.C-A-E | ɸ-ɸ-E | C-A-E | 0 | F3 |  |  | 0 | 5
C71.A-B-E | ɸ-ɸ-E | A-B-E | 0 | F3 |  |  | 5 | 0
C71.B-C-E | ɸ-ɸ-E | B-C-E | 0 | F3 |  |  | 5 | 0
C71.C-A-E | ɸ-ɸ-E | C-A-E | 0 | F3 |  |  | 5 | 0
C72.A-B-E | ɸ-ɸ-E | A-B-E | 0 | F3 |  |  | 5 | 5
C72.B-C-E | ɸ-ɸ-E | B-C-E | 0 | F3 |  |  | 5 | 5
C72.C-A-E | ɸ-ɸ-E | C-A-E | 0 | F3 |  |  | 5 | 5
C73.A-B-E | ɸ-ɸ-E | A-B-E | 90 | F3 |  |  | 5 | 5
C73.B-C-E | ɸ-ɸ-E | B-C-E | 90 | F3 |  |  | 5 | 5
C73.C-A-E | ɸ-ɸ-E | C-A-E | 90 | F3 |  |  | 5 | 5
C74.A-B-E | ɸ-ɸ-E | A-B-E | 90 | F3 |  |  | 5 | 10
C74.B-C-E | ɸ-ɸ-E | B-C-E | 90 | F3 |  |  | 5 | 10
C74.C-A-E | ɸ-ɸ-E | C-A-E | 90 | F3 |  |  | 5 | 10
C75.A-B-E | ɸ-ɸ-E | A-B-E | 180 | F3 |  |  | 5 | 10
C75.B-C-E | ɸ-ɸ-E | B-C-E | 180 | F3 |  |  | 5 | 10
C75.C-A-E | ɸ-ɸ-E | C-A-E | 180 | F3 |  |  | 5 | 10
C76.A-B-E | ɸ-ɸ-E | A-B-E | 0 | F4 |  |  | 0 | 0
C76.B-C-E | ɸ-ɸ-E | B-C-E | 0 | F4 |  |  | 0 | 0
C76.C-A-E | ɸ-ɸ-E | C-A-E | 0 | F4 |  |  | 0 | 0
C77.A-B-E | ɸ-ɸ-E | A-B-E | 0 | F4 |  |  | 0 | 5
C77.B-C-E | ɸ-ɸ-E | B-C-E | 0 | F4 |  |  | 0 | 5
C77.C-A-E | ɸ-ɸ-E | C-A-E | 0 | F4 |  |  | 0 | 5
C78.A-B-E | ɸ-ɸ-E | A-B-E | 0 | F4 |  |  | 5 | 0
C78.B-C-E | ɸ-ɸ-E | B-C-E | 0 | F4 |  |  | 5 | 0
C78.C-A-E | ɸ-ɸ-E | C-A-E | 0 | F4 |  |  | 5 | 0
C79.A-B-E | ɸ-ɸ-E | A-B-E | 0 | F4 |  |  | 5 | 5
C79.B-C-E | ɸ-ɸ-E | B-C-E | 0 | F4 |  |  | 5 | 5
C79.C-A-E | ɸ-ɸ-E | C-A-E | 0 | F4 |  |  | 5 | 5
C80.A-B-E | ɸ-ɸ-E | A-B-E | 90 | F4 |  |  | 5 | 5
C80.B-C-E | ɸ-ɸ-E | B-C-E | 90 | F4 |  |  | 5 | 5
C80.C-A-E | ɸ-ɸ-E | C-A-E | 90 | F4 |  |  | 5 | 5
C81.A-B-E | ɸ-ɸ-E | A-B-E | 90 | F4 |  |  | 5 | 10
C81.B-C-E | ɸ-ɸ-E | B-C-E | 90 | F4 |  |  | 5 | 10
C81.C-A-E | ɸ-ɸ-E | C-A-E | 90 | F4 |  |  | 5 | 10
C82.A-B-E | ɸ-ɸ-E | A-B-E | 180 | F4 |  |  | 5 | 10
C82.B-C-E | ɸ-ɸ-E | B-C-E | 180 | F4 |  |  | 5 | 10
C82.C-A-E | ɸ-ɸ-E | C-A-E | 180 | F4 |  |  | 5 | 10
C83.A-B-E | ɸ-ɸ-E | A-B-E | 0 | F5 |  |  | 5 | 0
C83.B-C-E | ɸ-ɸ-E | B-C-E | 0 | F5 |  |  | 5 | 0
C83.C-A-E | ɸ-ɸ-E | C-A-E | 0 | F5 |  |  | 5 | 0
C84.A-B-E | ɸ-ɸ-E | A-B-E | 0 | F5 |  |  | 5 | 5
C84.B-C-E | ɸ-ɸ-E | B-C-E | 0 | F5 |  |  | 5 | 5
C84.C-A-E | ɸ-ɸ-E | C-A-E | 0 | F5 |  |  | 5 | 5
C85.A-B-E | ɸ-ɸ-E | A-B-E | 90 | F5 |  |  | 5 | 5
C85.B-C-E | ɸ-ɸ-E | B-C-E | 90 | F5 |  |  | 5 | 5
C85.C-A-E | ɸ-ɸ-E | C-A-E | 90 | F5 |  |  | 5 | 5
C86.A-B-E | ɸ-ɸ-E | A-B-E | 90 | F5 |  |  | 5 | 10
C86.B-C-E | ɸ-ɸ-E | B-C-E | 90 | F5 |  |  | 5 | 10
C86.C-A-E | ɸ-ɸ-E | C-A-E | 90 | F5 |  |  | 5 | 10
| Tests | x5
Model A1 |  |  |  | Key: | [5 empty] | Notes:
C3 Count: | 63 | 315 |  | Rf - | Fault Resistance |  | (ohms) |  |  | (1) phase-to-phase-to-earth faults with a resistance
|  |  |  | ɸ - | Phase |  | (A, B, C) or (L1, L2, L3) |  |  | between the phases shall have only one phase earthed.
|  |  |  | E - | Earth

## Table C.4_Three Phase
ENA TS 48-6-1, Dynamic Tests - Three Phase Faults
Test Reference | Fault Type | Phases | POW (Deg.) | Fault Location | Fault Level | Load Flow (MW) | Rf (W) | Test Results
[8 empty] | Test 1 |  | Test 2 |  | Test 3 |  | Test 4 |  | Test 5 |  | Min. Operate Time | Max. Operate Time | Ave. Operate Time
[8 empty] | Operate Time | Prot. Element | Operate Time | Prot. Element | Operate Time | Prot. Element | Operate Time | Prot. Element | Operate Time | Prot. Element
C87.A-B-C | 3ɸ | A-B-C | 0 | F1 |  |  | 0
C88.A-B-C | 3ɸ | A-B-C | 90 | F1 |  |  | 0
C89.A-B-C | 3ɸ | A-B-C | 0 | F1 |  |  | 2
C90.A-B-C | 3ɸ | A-B-C | 0 | F2 |  |  | 0
C91.A-B-C | 3ɸ | A-B-C | 90 | F2 |  |  | 0
C92.A-B-C | 3ɸ | A-B-C | 0 | F2 |  |  | 2
C93.A-B-C | 3ɸ | A-B-C | 0 | F3 |  |  | 0
C94.A-B-C | 3ɸ | A-B-C | 90 | F3 |  |  | 0
C95.A-B-C | 3ɸ | A-B-C | 180 | F3 |  |  | 0
C96.A-B-C | 3ɸ | A-B-C | 0 | F3 |  |  | 1
C97.A-B-C | 3ɸ | A-B-C | 0 | F3 |  |  | 2
C98.A-B-C | 3ɸ | A-B-C | 0 | F4 |  |  | 0
C99.A-B-C | 3ɸ | A-B-C | 90 | F4 |  |  | 0
C100.A-B-C | 3ɸ | A-B-C | 180 | F4 |  |  | 0
C101.A-B-C | 3ɸ | A-B-C | 0 | F4 |  |  | 1
C102.A-B-C | 3ɸ | A-B-C | 0 | F4 |  |  | 2
C103.A-B-C | 3ɸ | A-B-C | 0 | F5 |  |  | 0
C104.A-B-C | 3ɸ | A-B-C | 90 | F5 |  |  | 0
C105.A-B-C | 3ɸ | A-B-C | 0 | F5 |  |  | 2
| Tests | x5
Model A1 |  |  |  | Key:
C4 Count: | 19 | 95 |  | Rf - | Fault Resistance |  | (ohms)
|  |  |  | ɸ - | Phase |  | (A, B, C) or (L1, L2, L3)
|  |  |  | E - | Earth

## Table C.5_SOTF
ENA TS 48-6-1, Dynamic Tests - Switch on to Fault
Test Reference | Fault Type | Phase(s) | POW (Deg.) | Fault Location | Fault Level | Rf (W) | Test Results
[7 empty] | Test 1 |  | Test 2 |  | Test 3 |  | Test 4 |  | Test 5 |  | Min. Operate Time | Max. Operate Time | Ave. Operate Time
[7 empty] | Operate Time | Prot. Element | Operate Time | Prot. Element | Operate Time | Prot. Element | Operate Time | Prot. Element | Operate Time | Prot. Element
C106.A-E | ɸ-E | A-E | 0 | F1 |  | 0
C106.B-E | ɸ-E | B-E | 0 | F1 |  | 0
C106.C-E | ɸ-E | C-E | 0 | F1 |  | 0
C107.A-E | ɸ-E | A-E | 0 | F1 |  | 5
C107.B-E | ɸ-E | B-E | 0 | F1 |  | 5
C107.C-E | ɸ-E | C-E | 0 | F1 |  | 5
C108.A-B-C | 3ɸ | A-B-C | 90 | F1 |  | 0
C109.A-B | ɸ-ɸ | A-B | 0 | F1 |  | 0
C109.B-C | ɸ-ɸ | B-C | 0 | F1 |  | 0
C109.C-A | ɸ-ɸ | C-A | 0 | F1 |  | 0
C110.A-B-C | 3ɸ | A-B-C | 90 | F2 |  | 0
C111.A-E | ɸ-E | A-E | 0 | F3 |  | 0
C111.B-E | ɸ-E | B-E | 0 | F3 |  | 0
C111.C-E | ɸ-E | C-E | 0 | F3 |  | 0
C112.A-E | ɸ-E | A-E | 0 | F3 |  | 2
C112.B-E | ɸ-E | B-E | 0 | F3 |  | 2
C112.C-E | ɸ-E | C-E | 0 | F3 |  | 2
C113.A-B-C | 3ɸ | A-B-C | 90 | F4 |  | 0
C114.A-B-C | 3ɸ | A-B-C | 90 | F4 |  | 0
| Tests | x5
Model A1 |  |  |  | Key:
C5 Count: | 19 | 95 |  | Rf - | Fault Resistance |  | (ohms)
|  |  |  | ɸ - | Phase |  | (A, B, C) or (L1, L2, L3)
|  |  |  | E - | Earth

## Table C.6_Evolving & X Country
ENA TS 48-6-1, Dynamic Tests - Evolving & Cross-Country Faults
Test Reference | Initial Fault | [6 empty] | Final Fault |  |  | Rf (W) |  | Test Results
| Fault Type | Phase(s) | Evolving Times (ms) | POW (Deg.) | Location | Fault Level | Load Flow (MW) | Fault Type | Phase(s) | Location | ɸ-ɸ | ɸ-E(5) | Test 1 |  | Test 2 |  | Test 3 |  | Test 4 |  | Test 5 |  | Min. Opertate Time | Max. Operate Time | Ave. Operate Time
[13 empty] | Operate Time | Prot. Element | Operate Time | Prot. Element | Operate Time | Prot. Element | Operate Time | Prot. Element | Operate Time | Prot. Element
C115.A-E.B | ɸ-E | A-E | 5 | 0 | F3 |  |  | ɸ-ɸ-E | A-B-E | F3 | 5 | 0
C115.B-E.C | ɸ-E | B-E | 5 | 0 | F3 |  |  | ɸ-ɸ-E | B-C-E | F3 | 5 | 0
C115.C-E.A | ɸ-E | C-E | 5 | 0 | F3 |  |  | ɸ-ɸ-E | C-A-E | F3 | 5 | 0
C116.A-E.B | ɸ-E | A-E | 40 | 0 | F3 |  |  | ɸ-ɸ-E | A-B-E | F3 | 5 | 0
C116.B-E.C | ɸ-E | B-E | 40 | 0 | F3 |  |  | ɸ-ɸ-E | B-C-E | F3 | 5 | 0
C116.C-E.A | ɸ-E | C-E | 40 | 0 | F3 |  |  | ɸ-ɸ-E | C-A-E | F3 | 5 | 0
C117.A-E.B | ɸ-E | A-E | 5 | 90 | F3 |  |  | ɸ-ɸ-E | A-B-E | F3 | 5 | 0
C117.B-E.C | ɸ-E | B-E | 5 | 90 | F3 |  |  | ɸ-ɸ-E | B-C-E | F3 | 5 | 0
C117.C-E.A | ɸ-E | C-E | 5 | 90 | F3 |  |  | ɸ-ɸ-E | C-A-E | F3 | 5 | 0
C118.A-E.B | ɸ-E | A-E | 40 | 90 | F3 |  |  | ɸ-ɸ-E | A-B-E | F3 | 5 | 0
C118.B-E.C | ɸ-E | B-E | 40 | 90 | F3 |  |  | ɸ-ɸ-E | B-C-E | F3 | 5 | 0
C118.C-E.A | ɸ-E | C-E | 40 | 90 | F3 |  |  | ɸ-ɸ-E | C-A-E | F3 | 5 | 0
C119.A-E.B | ɸ-E | A-E | 5 | 0 | F4 |  |  | ɸ-ɸ-E | A-B-E | F4 | 0 | 0
C119.B-E.C | ɸ-E | B-E | 5 | 0 | F4 |  |  | ɸ-ɸ-E | B-C-E | F4 | 0 | 0
C119.C-E.A | ɸ-E | C-E | 5 | 0 | F4 |  |  | ɸ-ɸ-E | C-A-E | F4 | 0 | 0
C120.A-E.B | ɸ-E | A-E | 40 | 0 | F4 |  |  | ɸ-ɸ-E | A-B-E | F4 | 0 | 0
C120.B-E.C | ɸ-E | B-E | 40 | 0 | F4 |  |  | ɸ-ɸ-E | B-C-E | F4 | 0 | 0
C120.C-E.A | ɸ-E | C-E | 40 | 0 | F4 |  |  | ɸ-ɸ-E | C-A-E | F4 | 0 | 0
C121.A-E.B | ɸ-E | A-E | 5 | 90 | F4 |  |  | ɸ-ɸ-E | A-B-E | F4 | 5 | 0
C121.B-E.C | ɸ-E | B-E | 5 | 90 | F4 |  |  | ɸ-ɸ-E | B-C-E | F4 | 5 | 0
C121.C-E.A | ɸ-E | C-E | 5 | 90 | F4 |  |  | ɸ-ɸ-E | C-A-E | F4 | 5 | 0
C122.A-E.B | ɸ-E | A-E | 40 | 90 | F4 |  |  | ɸ-ɸ-E | A-B-E | F4 | 5 | 0
C122.B-E.C | ɸ-E | B-E | 40 | 90 | F4 |  |  | ɸ-ɸ-E | B-C-E | F4 | 5 | 0
C122.C-E.A | ɸ-E | C-E | 40 | 90 | F4 |  |  | ɸ-ɸ-E | C-A-E | F4 | 5 | 0
C123.A-B.C | ɸ-ɸ | A-B | 5 | 0 | F3 |  |  | 3ɸ | A-B-C | F3 | 0 | -
C123.B-C.A | ɸ-ɸ | B-C | 5 | 0 | F3 |  |  | 3ɸ | A-B-C | F3 | 0 | -
C123.C-A.B | ɸ-ɸ | C-A | 5 | 0 | F3 |  |  | 3ɸ | A-B-C | F3 | 0 | -
C124.A-B.C | ɸ-ɸ | A-B | 40 | 0 | F3 |  |  | 3ɸ | A-B-C | F3 | 0 | -
C124.B-C.A | ɸ-ɸ | B-C | 40 | 0 | F3 |  |  | 3ɸ | A-B-C | F3 | 0 | -
C124.C-A.B | ɸ-ɸ | C-A | 40 | 0 | F3 |  |  | 3ɸ | A-B-C | F3 | 0 | -
C125.A-B.C | ɸ-ɸ | A-B | 5 | 90 | F2 |  |  | 3ɸ | A-B-C | F2 | 2 | 0
C125.B-C.A | ɸ-ɸ | B-C | 5 | 90 | F2 |  |  | 3ɸ | A-B-C | F2 | 2 | 0
C125.C-A.C | ɸ-ɸ | C-A | 5 | 90 | F2 |  |  | 3ɸ | A-B-C | F2 | 2 | 0
C126.A-B.C | ɸ-ɸ | A-B | 40 | 90 | F2 |  |  | 3ɸ | A-B-C | F2 | 2 | 0
C126.B-C.A | ɸ-ɸ | B-C | 40 | 90 | F2 |  |  | 3ɸ | A-B-C | F2 | 2 | 0
C126.C-A.C | ɸ-ɸ | C-A | 40 | 90 | F2 |  |  | 3ɸ | A-B-C | F2 | 2 | 0
C127.A-E(3) | ɸ-E | A-E | 5 | 90 | F3 |  |  | ɸ-E | A-E | F6 | - | 0
C127.B-E(3) | ɸ-E | B-E | 5 | 90 | F3 |  |  | ɸ-E | B-E | F6 | - | 0
C127.C-E(3) | ɸ-E | C-E | 5 | 90 | F3 |  |  | ɸ-E | C-E | F6 | - | 0
C128.A-E(3) | ɸ-E | A-E | 40 | 90 | F3 |  |  | ɸ-E | A-E | F6 | - | 0
C128.B-E(3) | ɸ-E | B-E | 40 | 90 | F3 |  |  | ɸ-E | B-E | F6 | - | 0
C128.C-E(3) | ɸ-E | C-E | 40 | 90 | F3 |  |  | ɸ-E | C-E | F6 | - | 0
C129.A-E.B(4) | ɸ-E | A-E | 5 | 0 | F3 |  |  | ɸ-E | B-E | F6 | - | 0
C129.B-E.C(4) | ɸ-E | B-E | 5 | 0 | F3 |  |  | ɸ-E | C-E | F6 | - | 0
C129.C-E.A(4) | ɸ-E | C-E | 5 | 0 | F3 |  |  | ɸ-E | A-E | F6 | - | 0
C130.A-E.B(4) | ɸ-E | A-E | 40 | 0 | F3 |  |  | ɸ-E | B-E | F6 | - | 0
C130.B-E.C(4) | ɸ-E | B-E | 40 | 0 | F3 |  |  | ɸ-E | C-E | F6 | - | 0
C130.C-E.A(4) | ɸ-E | C-E | 40 | 0 | F3 |  |  | ɸ-E | A-E | F6 | - | 0
C131.A-E(3) | ɸ-E | A-E | 5 | 0 | F6 |  |  | ɸ-E | A-E | F3 | - | 0
C131.B-E(3) | ɸ-E | B-E | 5 | 0 | F6 |  |  | ɸ-E | B-E | F3 | - | 0
C131.C-E(3) | ɸ-E | C-E | 5 | 0 | F6 |  |  | ɸ-E | C-E | F3 | - | 0
C132.A-E(3) | ɸ-E | A-E | 40 | 0 | F6 |  |  | ɸ-E | A-E | F3 | - | 0
C132.B-E(3) | ɸ-E | B-E | 40 | 0 | F6 |  |  | ɸ-E | B-E | F3 | - | 0
C132.C-E(3) | ɸ-E | C-E | 40 | 0 | F6 |  |  | ɸ-E | C-E | F3 | - | 0
C133.A-E.B(4) | ɸ-E | A-E | 5 | 0 | F6 |  |  | ɸ-E | B-E | F3 | - | 0
C133.B-E.C(4) | ɸ-E | B-E | 5 | 0 | F6 |  |  | ɸ-E | C-E | F3 | - | 0
C133.C-E.A(4) | ɸ-E | C-E | 5 | 0 | F6 |  |  | ɸ-E | A-E | F3 | - | 0
C134.A-E.B(4) | ɸ-E | A-E | 40 | 0 | F6 |  |  | ɸ-E | B-E | F3 | - | 0
C134.B-E.C(4) | ɸ-E | B-E | 40 | 0 | F6 |  |  | ɸ-E | C-E | F3 | - | 0
C134.C-E.A(4) | ɸ-E | C-E | 40 | 0 | F6 |  |  | ɸ-E | A-E | F3 | - | 0
C135.A-E.B(4) | ɸ-E | A-E | 5 | 0 | F5 |  |  | ɸ-E | B-E | F2 | - | 0
C135.B-E.C(4) | ɸ-E | B-E | 5 | 0 | F5 |  |  | ɸ-E | C-E | F2 | - | 0
C135.C-E.A(4) | ɸ-E | C-E | 5 | 0 | F5 |  |  | ɸ-E | A-E | F2 | - | 0
C136.A-E.B(4) | ɸ-E | A-E | 40 | 0 | F5 |  |  | ɸ-E | B-E | F2 | - | 0
C136.B-E.C(4) | ɸ-E | B-E | 40 | 0 | F5 |  |  | ɸ-E | C-E | F2 | - | 0
C136.C-E.A(4) | ɸ-E | C-E | 40 | 0 | F5 |  |  | ɸ-E | A-E | F2 | - | 0
| Tests | x5
Model A1 |  |  |  | Key: | [6 empty] | Notes:
C6 Count: | 66 | 330 |  | Rf - | Fault Resistance |  | (ohms) |  |  |  | 1) Faults C115 to C126 are Evolving Faults
|  |  |  | ɸ - | Phase |  | (L1, L2, L3) or (A, B, C) |  |  |  | 2) Faults C127 to C136 are Cross-Country Faults
|  |  |  | E - | Earth | [5 empty] | 3) Initial Fault and Final Faults are on the same phase
4) Initial Fault and Final Faults are on different phases
5) Evolving phase-to-phase-to-earth faults with a resistance
between the phases shall have only one phase earthed.