## Amend 1.
2. Power Quality – Harmonics:
Power Generating Module tested to BS EN 61000-3-2
Prated |  |  | 3.6 kVA
Harmonics | 50%Prated |  | 100% Prated |  | Limits
| Amps | % | Amps | % | 1 phase
2 | 0.091 | 0.85% | 0.157 | 0.73% | 1.08
3 | 0.158 | 1.48% | 0.309 | 1.44% | 2.3
4 | 0.018 | 0.17% | 0.027 | 0.13% | 0.43
5 | 0.063 | 0.59% | 0.074 | 0.35% | 1.14
6 | 0.019 | 0.18% | 0.023 | 0.11% | 0.3
7 | 0.055 | 0.51% | 0.076 | 0.36% | 0.77
8 | 0.011 | 0.1% | 0.007 | 0.03% | 0.23
9 | 0.039 | 0.36% | 0.052 | 0.24% | 0.4
10 | 0.009 | 0.08% | 0.011 | 0.05% | 0.184
11 | 0.045 | 0.42% | 0.044 | 0.21% | 0.33
12 | 0.012 | 0.11% | 0.016 | 0.07% | 0.153
13 | 0.034 | 0.32% | 0.036 | 0.17% | 0.21
14 | 0.031 | 0.29% | 0.055 | 0.26% | 0.131
15 | 0.072 | 0.67% | 0.085 | 0.4% | 0.15
16 | 0.053 | 0.5% | 0.064 | 0.3% | 0.115
17 | 0.062 | 0.58% | 0.074 | 0.35% | 0.132
18 | 0.053 | 0.49% | 0.061 | 0.29% | 0.102
19 | 0.054 | 0.51% | 0.065 | 0.3% | 0.118
20 | 0.046 | 0.43% | 0.054 | 0.25% | 0.092
21 | 0.055 | 0.51% | 0.064 | 0.3% | 0.107
22 | 0.041 | 0.38% | 0.048 | 0.22% | 0.084
23 | 0.049 | 0.46% | 0.057 | 0.27% | 0.098
24 | 0.043 | 0.4% | 0.049 | 0.23% | 0.077
25 | 0.043 | 0.4% | 0.051 | 0.24% | 0.09
26 | 0.038 | 0.36% | 0.044 | 0.2% | 0.071
27 | 0.045 | 0.42% | 0.052 | 0.24% | 0.083
28 | 0.034 | 0.31% | 0.039 | 0.18% | 0.066
29 | 0.041 | 0.38% | 0.047 | 0.22% | 0.078
30 | 0.036 | 0.34% | 0.041 | 0.19% | 0.061
31 | 0.036 | 0.34% | 0.042 | 0.2% | 0.073
32 | 0.033 | 0.31% | 0.037 | 0.17% | 0.058
33 | 0.039 | 0.37% | 0.044 | 0.21% | 0.068
34 | 0.029 | 0.27% | 0.033 | 0.15% | 0.054
35 | 0.035 | 0.33% | 0.04 | 0.19% | 0.064
36 | 0.032 | 0.3% | 0.036 | 0.17% | 0.051
37 | 0.032 | 0.3% | 0.036 | 0.17% | 0.061
38 | 0.029 | 0.27% | 0.032 | 0.15% | 0.048
39 | 0.035 | 0.33% | 0.039 | 0.18% | 0.058
40 | 0.026 | 0.24% | 0.029 | 0.14% | 0.046
THD1 | 0.221 | 2.89% | 0.355 | 2.13% | 5%
PWHD2 | 0.438 | 2.19% | 0.596 | 2.98% | 23%
1 THD = Total Harmonic Distortion
2 PWHD = Partial Weighted Harmonic Distortion

## Amend 2.
4. Power quality – DC injection:
Output power | 20% | 50% | 75% | 100%
Test value(A) | 23.8mA | 27.1mA | 31.2mA | 34.8mA
Test value(%) | 0.11% | 0.12% | 0.14% | 0.16%
Limit | 0.25% | 0.25% | 0.25% | 0.25%

## Amend 3.
9. Limited Frequency Sensitive Mode – Over frequency test: The test should be carried out using the specific threshold frequency of 50.4 Hz and Drop of 10%.
2. Measurement a) to g): Active power output 60% after freezing = 100% Pemax S=5% (40% PEmax / Hz), threshold frequency for start/return: 50.4Hz
Frequency | 50.00Hz | 50.45Hz | 50.70Hz | 51.15Hz | 50.70Hz | 50.45Hz | 50.00Hz
Calculated P | 2160W | 2088W | 1728W | 1080W | 1728W | 2088W | 2160W
Measured P | 2134W | 2095W | 1739W | 1090W | 1740W | 2073W | 2168W
ΔP（%） | N/A | 0.19% | 0.31% | 0.28% | 0.33% | -0.42% | N/A
Limit ΔP/P1min: | ± 10 % of PEmax

## Amend 4.
10. Power output with falling frequency test: This test should be carried out in accordance with EN 50438 Annex D.3.2 active power feed-in at under-frequency.
Test sequence | Measured active power output | Frequency | Primary power source
Test a) 50 Hz ± 0.01 Hz | 3588 W | 50.01 Hz | 4500 W
Test b) Point between 49.5 Hz and 49.6 Hz | 3580 W | 50.01 Hz | 4500 W
Test c) Point between 47.5 Hz and 47.6 Hz | 3585 W | 50.01 Hz | 4500 W